## Slide 1
Framingham Public Schools
Fuller / Farley
Pre-Feasibility Study
Overview
Thursday, October 6, 2016
Fuller Middle School
Farley Middle School
BARGMANN HENDRIE + ARCHETYPE, INC.

## Slide 2
Pre-Feasibility Study
Assess Fuller and Farley Building Conditions
Conditions Assessments and Recommendations
Repairs v. Comprehensive Renovation
Required Code and Accessibility Upgrades
Site Issues
Evaluate Options for Renovation / New Construction
  Renovation / Hybrid / New Construction
Assist with MSBA Process
Identify requirements and process
Help prepare relevant information

## Slide 3
Fuller Building

## Slide 4: Fuller Middle School
Built in 1958
Formerly Framingham South High School
Single Story, 196,000 SF Building
  Cast-in-place concrete structure on pile foundation
Fuller MS uses ~160,000 SF 447 Students
Non-school uses ~36,000 SF
  Buildings & Grounds
  Framingham Public Access TV
  ACCEPT Transportation
  ESL Program Offices

## Slide 5
Existing 196,000 SF Fuller Middle School

## Slide 6
Fuller Building
Roof has organic growth, poor drainage and ongoing leaks
Roof warranty expires in 2014
Moisture has affected roof structure and interior spaces
    Users complain of odors
$4M estimated cost for roofing replacement
    30% structural roof deck replacement additional

## Slide 7
Fuller Building
Building is on concrete pile foundation
Crawl space below first floor is used to route MEP systems piping
Floor slab has rusted reinforcing and spalled concrete.
Repairs & insulation required

## Slide 8
Fuller Building
Original 1950’s aluminum windows are deteriorating.
Heat-loss and solar-gain through single glazing increases energy consumption
Renovation would require full window replacement

## Slide 9
Fuller Building
Masonry cracks allow moisture to enter the building
Inadequate masonry expansion joints exacerbate deterioration
Water infiltration has caused concrete spalling and brick deterioration

## Slide 10
Fuller Building
Doors, hardware, and other components do not meet MAAB and ADA accessibility requirements
Built-in casework is not accessible
Full renovation would require building to meet MAAB accessibility requirements

## Slide 11
Fuller Building
Conclusions:
Building systems are at the end of useful life
Systems will be increasingly costly to maintain
    Repairs more frequent and extensive
Code compliance will require costly work
5-year Capital Requirements could exceed $10 Million
  Concrete & Masonry $2,750,000
  Roofing $4,000,000
  Furnishings $ 800,000
  Fire Suppression $1,000,000
  HVAC $ 650,000
  Electrical $ 200,000
  Utilities & Site Improvements $ 850,000

## Slide 12
Farley Building

## Slide 13: Farley Building
Built in 1973 as Junior High School
  Identical layout to Barbieri and Cameron (before 2000 renovation)
Currently leased to Mass Bay Community College
2-story, 114,000 SF Building with split-levels
10,000 SF Pool area is unused

## Slide 14
Farley Building
Roof above pool wing requires replacement
Exterior wood panels are rotted and require replacement
Windows are generally serviceable
Masonry is in good condition

## Slide 15
Farley Building
Some accessibility compliance work has been done at toilet rooms
Clearances at doors are difficult to achieve with existing partitions
Guardrails are non-compliant and require retrofit

## Slide 16
Farley Building
The abandoned swimming pool leaks groundwater into pool
10,000 SF requires full renovation into non-pool usable space
    Kitchen
    Cafeteria

## Slide 17
Farley Building
Conclusions:
Building is in reasonably sound condition
Work will be required to update and maintain building
Pool, accessibility upgrades and life safety are significant capital projects
5-year Capital Requirements approach $5 Million
  Superstructure & Exterior Envelope $1,600,000
  Roofing $ 200,000
  Interior Construction (kitchen, cafeteria, MAAB) $1,500,000
  Fire Suppression $ 600,000
  Plumbing $ 750,000
  Electrical $ 350,000
  Utilities & Site Improvements $ 50,000

## Slide 18
Redevelopment Options
Site Constraints
Fuller Middle School 120,000 SF ~700 Students
    100% Renovation
    100% New
    Hybrid – Renovate core; new classrooms
Farley Middle School 120,000 SF ~700 Students
    100% Renovation
    100% New
    Hybrid – Renovate core; new classrooms
K-8 Options 196,000 SF ~1,250 Students
    Single School
    Farley Middle School with Fuller Elementary School

## Slide 19
Site Constraints
Zoning
Wetlands
Parking

## Slide 20
Zoning Issues
Property area includes Muster fields
Zoning By-Law dictates
Maximum building height
Maximum lot coverage
Setback requirements
Parking requirements

## Slide 21
Site Aerial

## Slide 22
Stream and Wetlands

## Slide 23
Buildable Area

## Slide 24
Existing Parking

## Slide 25
Parking Issues
Middle School w/ 700 students
    160 staff requires approximately 145-170 spaces plus visitor parking
ESL program and evening school uses drive higher need
Desire to relocate parking for 76 buses and 70 bus-driver cars, possibly to this site

## Slide 26
Buildable area is limited to existing building footprints and parking areas between Fuller and Farley
3-story, 35 foot height limitation imposed by zoning
Parking demand must be taken into account
Existing non-school users need a home, too
Site Limitations

## Slide 27
Program Issues
School | Total Size (GSF) | Students | GSF per student
Existing Fuller Middle School Program | 160,000 * | 447 | 358
MSBA Program Template (675 students) | 98,400 | 675 | 146
Walsh Middle School | 201,000 | 701 | 287
Cameron Middle School | 114,000 | 563 | 202
Program for New / Renovated Middle School | 120,000 | 650-800 | 150-185
*196,000 gsf – 36,000 gsf non-middle school uses. |  |  | 

## Slide 28
Existing 196,000 SF Fuller Middle School

## Slide 29
Renovated 120,000 SF Fuller Middle School

## Slide 30
Renovated 120,000 SF Fuller Middle School

## Slide 31
Hybrid 120,000 SF Fuller Middle School

## Slide 32
New 120,000 SF Fuller Middle School

## Slide 33
Alternate New 120,000 SF Fuller MS

## Slide 34
Existing 114,000 SF Farley Building

## Slide 35
Renovated 120,000 SF Farley Middle School

## Slide 36
Hybrid 120,000 SF Farley Middle School

## Slide 37
New 120,000 SF Farley Middle School

## Slide 38
Hybrid Farley MS and New Fuller ES

## Slide 39
New 196,000 SF Fuller K-8

## Slide 40: MSBA Process

## Slide 41: Questions?